# ME 354 Tutorial #9 							Winter 2001

# Non-Reacting Mixtures – Psychrometrics Applied to a Cooling Tower

Water exiting the condenser of a power plant at 45C enters a cooling tower with a mass flow rate of 15000 kgw/s. A stream of cooled water is returned to the condenser from the cooling tower with the same flow rate. Make-up water is added in a separate stream at 20C. Atmospheric air enters the cooling tower at 30C and a wet bulb temperature of 20C. The volumetric flow rate of air into the cooling tower is 8000 m3/s. Moist air exits the tower at 40C and 90% relative humidity. Assume an atmospheric pressure of 101.3 kPa.

Determine:

- the mass flow rate of dry air,

- the mass flow rate of make-up water, and

- the temperature of the cooled liquid water exiting the cooling tower.

Step 1: Draw a diagram to represent the system

# Step 2: Prepare a property table

# Step 3: State your assumptions

Assumptions:

- The cooling tower operates under steady conditions

- KE, PE  0

- Cooling tower is rigid Wcv = 0.

- Heat transfer with the surroundings is neglected

- Assume all liquid is saturated

- The pressure is constant throughout the cooling tower at 101.3 kPa.

Step 4: Calculations

Part a)

The mass flow rate of dry air can be determined using the volumetric flow rate of air into the cooling tower (given in the problem as 8000 m3/s) and the specific volume of this air as shown in Eq1.

ma,3=Va,3va,3					 (Eq1)

We can determine the specific volume of the air entering the cooling tower by determining the state point of location 3 on the psychrometric chart using Tdb,3 = 30C and Twb,3 = 20C.

From the psychrometric chart,

 va,3 = 0.873 m3/kga

Substituting this value and the given volumetric flow rate into Eq1 we can determine the mass flow rate of dry air.

→ma,3=Va,3va,3=8000m3s0.873m3kga= 9163.8 kga/s	Answer a)

Part b)

To determine the mass flow rate of the make-up water, denoted as mmw, we can perform a mass balance on the water entering/exiting our cooling tower control volume. At location 1 we have the stream of water entering the cooling tower from the condenser, which we will denote as mw,1. At location 2 we have the stream of water exiting the cooling tower to be returned to the condenser, which we will denote as mw,2. We are told in the problem statement that mw,1 = mw,2 = mw. At location 3, we have the moisture entering the cooling tower control volume carried in by the incoming air. We will denote this as mw,3. At location 4, we have the moisture leaving the cooling tower control volume carried out by the exiting air. We will denote this as mw,4. The mass balance on the water is performed in Eq2.

mw−mw+mw,3−mw,4+mmw=0→mmw=mw,4−mw,3		(Eq2)

We can express mw,3 & mw,4 in terms of the corresponding mass flow rates of  dry air at location 3 & 4 and their respective humidity ratios W3 & W4 as shown in Eq3 and Eq4.

mw,3=W3ma,3				(Eq3)

mw,4=W4ma,4				(Eq4)

Substituting Eq3 and Eq4 into Eq2 we obtain Eq5.

mmw=mw,4−mw,3=W4ma,4−W3ma,3			(Eq5)

From our assumption that the cooling tower operates in a steady manner, the mass flow rate of air will be constant i.e. ma,3 = ma,4 = ma. Eq5 can be rewritten as Eq6.

mmw=ma(W4−W3)				(Eq6)

Recall that we determined the mass flow rate of dry air in part a). We can determine the humidity ratio of the air entering the cooling tower by using state point 3 on the psychrometric chart.

From the psychrometric chart,

 W3 = 10.5 gw/kga = 0.0105 kgw/kga

Unfortunately, state point 4 (Tdb,4 = 40C & =90%) is off the psychrometric chart so we will have to calculate the value of W4 using equation 13-11b from Cengel and Boles as shown below.

From Table A-4 @ T= 40C, Psat = 7.384 kPa.

 W4=0.622φ4PsatP−φ4Psat=0.622(0.9)(7.384)101.3−0.9(7.384)=0.0437kgwkga

Substituting these values into Eq6, we can determine the mass flow rate of the make-up water.

→mmw=ma(W4−W3)=9163.8kgas0.0437−0.0105kgwkga

= 304 kgw/s	Answer b)

Part c)

We can determine the temperature of the cooled liquid water exiting the cooling tower by first determining its enthalpy. Since we are assuming it is a saturated liquid we can use the enthalpy to interpolate in Table A-4 to determine its temperature. To find the enthalpy of the water exiting the cooling tower we must perform an energy balance on the cooling tower control volume. At location 1, the rate of energy entering the control volume carried in by the stream of water coming from the condenser is mwhw,1, where h is used to denote enthalpy. At location 2 we have the stream of water leaving the cooling tower carrying away energy at a rate of mwhw,2. At location 3, the moist air carries energy at a rate of mah3 into the control volume. At location 4, we have moist air leaving the cooling tower control volume carrying energy out at a rate of mah4. The make-up water carries energy into the control volume at a rate of mmwhmw.  Combining all of these statements into one expression we obtain Eq7. Note: We have made use of our list of assumptions in developing Eq7.

mwhw,1−mwhw,2+mah3−mah4+mmwhmw=0 		(Eq7)

We can isolate the enthalpy of the water at location 2 by rearranging Eq7 as shown in Eq8.

hw,2=hw,1+ma(h3−h4)+mmwhmwmw 				(Eq8)

We have previously determined ma and mmw, and we are given mw in the problem statement.

hw,1

Since we have assumed saturated liquid water at location 1 we can determine hw,1 from Table A-4 using T1=45C.

 hw,1=188.45kJkgw

h3

Using state point 3 on the psychrometric chart we can determine h3.

 h3=57.5kJkga

h4

As stated previously, state point 4 is off the psychrometric chart so we must calculate h4. Using equation 13-1a from Cengel and Boles, we can calculate the enthalpy of DRY AIR alone.

 hdryair,4=1.005kJkga⋅C(40C)=40.2kJkga

We can calculate the enthalpy of the MOISTURE in the air using equation 13-4 from Cengel and Boles (or we can look it up in Table A-4 for hg @ T = 40C).

 hg,4=(2501.3+1.82(40))kJkgw=2574.1kJkgw

To combine the dry air and moisture enthalpies at location 4 into one term, h4, we need to convert the enthalpy of the moisture to be on a “per kg of dry air” basis by multiplying it by the humidity ratio, W4.

 h4=hdryair,4+W4hg,4=40.2kJkga+0.0437kgwkga2574.1kJkgw=152.7kJkga

hmw

Since we have assumed saturated liquid water at location 5 we can determine hmw from Table A-4 using T5=20C.

 hmw=83.96kJkgw

Substituting these values into Eq8, we can determine the enthalpy of the water at location 2.

#### hw,2=188.45kJkgw+9163.8kgas(57.5−152.7)kJkga+(304)kgws(83.96)kJkgw15000kgws

 hw,2=188.45kJkgw−56.46kJkgw=131.99kJkgw

As stated previously, since we have assumed saturated liquid water at location 2 we can use hw,2 to find the corresponding temperature in Table A-4. From Table A-4 we find that hw,2 lies in between the enthalpies corresponding to temperatures of 30C and 35C. We can interpolate in between them to find the temperature of the water exiting the cooling tower.

131.99−125.79146.68−125.79=T2−30C35C−30C

T2 = 31.5C 	Answer c)

#### Step 5: Summary

- the mass flow rate of dry air is 9163.8 kga/s

- the mass flow rate of make-up water is 304 kgw/s, and

- the temperature of the cooled liquid water exiting the cooling tower is 31.5C.